## Slide 1
7.1 Wastewater Treatment Process
Consists of 4 main components
Preliminary treatment
Primary treatment
Secondary treatment
Treatment and disposal of sludge

## Slide 2
7.2 Preliminary Treatment
Purpose - protect the operation of the wastewater treatment plant
Screening
Screens remove large solids such as rags, sticks, plastics and similar materials from the wastewater.

## Slide 3
Shredding
In some plants, shredding devices are installed after the bar screen or as alternatives to screening.
Shredding devices reduce solids to a size that can enter the plant without causing mechanical problems or clogging.
The most common shredder is the comminutor

## Slide 4
Grit Removal
The purpose of grit removal is to remove the heavy inorganic solids, which could cause excessive mechanical wear.
Grit includes sand, gravel, clay, egg shells, coffee grounds, metal filings, seeds and other similiar materials

## Slide 5
2. Primary Treatment
  Consists of primary sedimentation (or settling) tank or clarifier.
  reduce organic loading to secondary treatment units
  remove 30% to 40% BOD
  remove 60% to 70% SS
  tanks either rectangular or circular in shape
  sludge removal mechanism required in tanks

## Slide 6
3. Secondary Treatment
Principles of Aerobic Biological Treatment:
Organic Matter [Food]
+
Oxygen  [CO2 + H2O + NH3 + NO3 + SO4 ] + sludge
+
Biomass [Microorganisms]

## Slide 7
Types of Biological Treatment Process
1. Attached Growth (or Fixed-film) : microorganisms present and reproduce on a media surface
e.g. trickling filter
2. Suspended Growth :
microorganisms present and reproduce in suspension
e.g. activated sludge, aerated lagoon

## Slide 8
Trickling filter

## Slide 9
Activated sludge

## Slide 10
Aerated lagoon

## Slide 11
Secondary Sedimentation / Clarifier
removal of solids before final discharge into receiving waters
sludge either return to aeration tank or treated before disposal
either rectangular or circular in shape
Surface overflow rate less than 30 m3/m2.day at average flow
Hydraulic Retention Time (HRT) : minimum 2 hours at peak flow

## Slide 13
Disinfection
destruction of disease causing organisms in sewage effluent
required where discharge have a detrimental effect on receiving water
chlorination most common (others include ultra-violet, ozonation)
operational skill required
chlorination chamber required