## Slide 1: WASTE STABILIZATION POND (WSP)

## Slide 4: WASTE STABILIZATION POND (WSP)
Advantages:
Simplicity
simple to construct
simple to operate and maintain
only unskilled labour is needed

## Slide 5
Low Cost
cheaper than other wastewater treatment processes
no need for expensive equipment
High Efficiency
BOD removals > 90%
Total nitrogen removals is 70-90%
Total phosphorus removal is 30-45%
Efficient in removing pathogens

## Slide 6
Types of WSP
Anaerobic pond
Facultative pond
Maturation pond

## Slide 7
Anaerobic Pond
2-5 m deep
Receive high organic loading (usually > 100 g BOD/m3 d) – contain no dissolved oxygen and no algae
Primary function is BOD removal
Retention times are short (e.g. 1 day)

## Slide 8
Facultative Pond
1-2 m deep
Two types:
1. Primary Facultative Pond
– receive raw wastewater.
2. Secondary Facultative Pond
– receive settled wastewater
(e.g. effluent from anaerobic pond)
The primary function is the removal of BOD

## Slide 9
3 zone exist:
A surface zone where aerobic bacteria and algae exist in a symbiotic relationship. The algae provide the bacteria with oxygen and the bacteria provide the algae with carbon dioxide.
An anaerobic bottom zone in which accumulated solids are decomposed by anaerobic bacteria.
An intermediate zone that is partly aerobic and partly anaerobic in which the decomposition of organic wastes is carried out by facultative bacteria.

## Slide 11
Maturation Pond
1-1.5 m deep
Receive the effluent from a facultative pond
Primary function is the removal of pathogens

## Slide 12
BOD Removal
in anaerobic ponds BOD removal is achieved by sedimentation of settleable solids
in secondary facultative ponds that receive settled water (anaerobic pond effluent), the remaining non-settleable BOD is oxidized by heterotrophic bacteria
in primary facultative ponds (receive raw wastewater), the above functions of anaerobic and secondary facultative ponds are combined
in maturation ponds only a small amount of BOD removal occurs

## Slide 13
Pathogen Removal
Bacteria
Faecal bacteria are mainly removed in facultative and especially maturation ponds
The principal mechanism for faecal bacteria removal are:
  1- Time and temperature
- Faecal bacteria die-off in ponds increase
with both time and temperature
  2- High pH
- Faecal bacteria (except Vibrio Cholerae) die
very quickly (within minutes) at pH>9
  3- High light intensity
- Light of wavelength 425 – 700 nm can
damage faecal bacteria

## Slide 14
Design of WSP
1. Anaerobic Pond
Volumetric BOD loading (g/m3d)
------- (1)
Where
Li = influent BOD, mg/L (=g/m3)
Q = flow, m3/d
= anaerobic pond volume, m3

## Slide 15
should lie between 100 and 400 g/m3d
to maintain anaerobic conditions
to avoid odour release
The mean hydraulic retention time (HRT), ta (day) is determined from:
--------- (2)

## Slide 16: Design values of permissible volumetric loading on and percentage BOD removal in anaerobic ponds at various temperatures
Temperature (oC) | Volumetric loading (g/m3d) | BOD removal(%)
<10 | 100 | 40
10 – 20 | 20T – 100 | 2T + 20
>20 | 300 | 60*

## Slide 17
2. Facultative Ponds
Surface BOD loading (s, kg.ha d)
------ (3)
where
Af = facultative pond area, m2
s = 10LiQ/Af

## Slide 18
The permissible BOD loading, s max
s max = 350 (1.107 – 0.002T)T-25 ----- (4)

## Slide 19
Once a suitable value of s has been selected, the pond area is calculated from equation (3) and its retention time (tf, day) from:
tf = AfD/Q ---------- (5)
Where
D = pond depth, m
Q = wastewater flow, m3/day

## Slide 20
3. Maturation Ponds
(a) Faecal Coliform Removal
The resulting equation for a single pond is:
Ne = Ni / (1 + kTt) -------- (6)

## Slide 21
Where
Ne = number of FC per 100 mL of effluent
Ni = number of FC per 100 mL of influent
kT = first order rate constant for FC removal, per day
t = retention time, day

## Slide 22
for a series of anaerobic, facultative and maturation ponds, equation (6) becomes:
--- (7)
Ne and Ni now refer to the numbers of FC per 100 mL of the final effluent and raw wastewater

## Slide 23
The value of kT is highly temperature dependent.
kT = 2.6 (1.19)T-20 ---------- (8)

## Slide 24
Check the BOD effluent concentration, le
--------- (9)
Where
le = BOD effluent concentration, mg/L
li = BOD influent concentration, mg/L
K1 = first order rate constant for BOD
removal, per day
t = retention time, day

## Slide 25
The value of K1 is highly temperature dependent
------ (10)
where
K1@ 20oC = 0.3 per day and
 = 1.05

## Slide 26
For n ponds in series, BOD effluent can be calculated as follows
------ (11)

## Slide 27: Example
Design a waste stabilization pond to treat 10,000 m3/day of a wastewater which has a BOD of 350 mg/L and 1x108 FC per 100 mL. The effluent should contain no more than 1000 FC per 100 mL and 20 mg/L BOD. The design temperature is 18oC.

## Slide 28
Solution
(a) Anaerobic Ponds
From Table the design loading is given by:
= 20T–100 = (20 x 18)-100 = 260 g/m3d
The pond volume is given by equation (1) as:
= LiQ/
= 350 x 10,000/260 = 13,462 m3

## Slide 29
The retention time is given by equation (2) as:
= 13,462 /10,000 = 1.35 day
The BOD removal is given in Table as:
R = 2T + 20 = (2 x 18) + 20 = 56 percent

## Slide 30
(b) Facultative Ponds
The design loading is given by equation (4) as:
s max = 350 (1.107 – 0.002T)T-25
= 350 (1.107 – 0.002T)T-25
= 350[1.107 – (0.002 x 18)]18-25
= 216 kg/ha d

## Slide 31
Thus the area is given by equation (3) as:
Af = 10 x 0.44 x 350 x 10,000/216
= 71,300 m2
s = 10LiQ / Af

## Slide 32
The retention time is given by equation (5) as:
tf = AfD/Q
Taking a depth of 1.5 m, this becomes:
tf = 71,300 x 1.5/10,000
= 10.7 day

## Slide 33
(c ) Maturation Ponds
Faecal Coliform Removal
For 18oC the value of kT is given by equation (8) as:
kT = 2.6 (1.19)T-20 = 2.6(1.19) -2 = 1.84 day-1

## Slide 34
The value of Ne is given by equation (7):
Taking tm = 7 days, this becomes:
For n = 1, Ne = 99957 > 1000 FC/100 mL
For n = 2, Ne = 7201 > 1000 FC/100 mL
For n = 3, Ne = 518 < 1000 FC/100 mL , OK

## Slide 35
For a depth of 1.5 m, the area of the maturation pond is
Am = Q tm /D
= 10,000 x 7/1.5
= 46,667 m2

## Slide 36
BOD Removal
Anaerobic Pond: le = 0.44 x 350 mg/L = 154 mg/L
Facultative and Maturation Pond:
= 1.6 mg/L