## Slide 1: 5.6 SEDIMENTATION
Objective
In this lesson we will answer the following questions:
How does sedimentation fit into the water treatment process?

## Slide 2
To remove the suspended material from water by the action of gravity
Sedimentation tanks can be rectangular, square or circular in shape. The most common types are rectangular, and circular with centre feed.

## Slide 3: SEDIMENTATION TANK
Sedimentation Tank

## Slide 6
Types of particle
a. Discrete / individual particle
-size, velocity are constant during the settling
b. Flocculate particle
- size, velocity are changing during the settling
- the particles flocculate and grow bigger in size

## Slide 7
Types of sedimentation
Type 1 sedimentation
- particles concentration is very low
- settle as individual particles
- example : sand and grit material removal in wastewater treatment process

## Slide 8
Type 2 sedimentation
- particles concentration is low
- particles flocculate during settling
- example : particles removal in sedimentation tank

## Slide 9
Type 3 sedimentation / zone sedimentation
- particles concentration is high
- particles tend to settle as a mass and form a layer called “blanket”
- distinct clear zone and sludge zone are present
- example : secondary sedimentation in wastewater treatment plant

## Slide 10
Sedimentation Concepts
s - settling velocity
o - over flow rate
o = =
Where
Q = flow rate
As = surface area
H = depth of water
t = detention time

## Slide 11
If s > o , particles will completely settle
If s < o , particles do not settle unless the particles are at h level when entering the sedimentation tank, where
h = s t
To get the effective of sedimentation tank,
o <<< s. This can be achieved by increasing
the area of the tank (o = Q/As)

## Slide 12
Type 2 Sedimentation Analysis
To determine the criteria of the particles and the effectiveness of the tank
Using settling column
  diameter of the column is not important but the depth of the water is same as the actual water depth
  occur in steady state

## Slide 13
Method
  record the initial concentration of the suspended solids, Co
  withdrawn the sample at every sample ports at selected time intervals, Ct
  calculate the percent of removal for every sample point and sampling time
  plot the %R at depth versus time graph

## Slide 14
From the analysis, can determine
  the effectiveness of the tank at selected time
  o = H
t
  As = Q
o

## Slide 15
Relationship between analysis (column) and actual condition (tank)
- Scale-up factors of 0.65 for overflow rate and 1.75 for detention time to be used to design the tank.

## Slide 16: Example 1
Given:
Co = 400 mg/L, Overflow rate = 2.7 m3/m2.hour
Find the effectiveness of settling column.
Time (t) | 5 | 10 | 20 | 40 | 60 | 90 | 120
Depth, m | Percent Removal (%R) |  |  |  |  |  | 
0.6 | 41 | 50 | 60 | 67 | 72 | 73 | 76
1.2 | 19 | 33 | 45 | 58 | 62 | 70 | 74
1.8 | 15 | 31 | 38 | 54 | 59 | 63 | 71

## Slide 17
Solution
1. o = H
t i
2. Plot the graph (%R at depth (H) vs Time (t))

## Slide 19
3. The effectiveness of settling column

## Slide 20
Example 2
Determine the surface area of settling tank for 0.5 m3/s and find the depth of the clarifier for the overflow rate of 32.5 m/d and detention time of 95 min. A minimum of two tanks is provided, each with a width of 12 m.

## Slide 21
Solution :

## Slide 22
Example 3
A rectangular sedimentation tank is to be designed for a flow of 20 million litre per day using a 2:1 length-width ratio and overflow rate of 24 m3/m2.day. the tank is to be 2 m deep. Determine the dimensions for the tank and the detention time.

## Slide 23
Solution
Dimensions
Q = AV
= 833.33 m2
L:W = 2:1
A = L x W = 2W x W = 2W2 = 833.33
W = 20.41m
L = 2W = 2(20.41) = 40.82 m

## Slide 24
Detention time
t = =
= 120 min = 0.0833 day

## Slide 25
An ideal rectangular sedimentation tank illustration the settling of discrete particles

## Slide 26
Long rectangular settling basin