## Slide 1: Water Treatment 4. Softening
Water Softening
  Hard water
  Hard water is usually defined as water which contains a high concentration of Ca++ and Mg++ ions.
  Water Softening
  Softening is the removal of hardness from water.
  Types of Hardness
    Carbonate hardness (Temporary Hardness)
      Calcium bicarbonate Ca(HCO3)2
      Magnesium bicarbonate Mg(HCO3)2
    Non-carbonate hardness (Permanent Hardness)
      Calcium sulfate and chloride
      Magnesium sulfate and chloride
  Classification of water according to its hardness:
  s
Soft | < 50 mg/L as CaCO3
Moderately Soft | 50 – 150 mg/L as CaCO3
Hard | > 150 – 300 mg/L as CaCO3
Very Hard | >300 mg/L as CaCO3

## Slide 2: Water Treatment 4. Softening
Hardness Impact
  Case water to form scales and resist to soap.
  Clog pipes
  Causes excessive use of soaps and detergents.
  Hard water harms many industrial processes.
  Ruin water heaters and boilers.
  Reduce heating efficiency.

## Slide 3: Water Treatment 4. Softening (Chemical Precipitation)
Water Softening Methods
  Chemical precipitation: [lime – soda ash softening]. By using lime Ca(OH)2 and soda ash Na2CO3
  Advantages:
    Aids in coagulation
    Aids in disinfection
    Help precipitates heavy metals.
  Disadvantages
    Large quantities of sludge

## Slide 4: Water Treatment 4. Softening (Chemical Precipitation)
Chemistry of Precipitation Softening
  Lime is added to remove carbonate hardness
  Soda ash is added to remove non-carbonate hardness
  CO2 is applied after lime treatment to lower pH (re-carbonation).
  Lime softening consists of raising the waters pH to produce calcium carbonate and magnesium hydroxide which settle out of the water.
  Lime Softening
  Ca(HCO3)2 + Ca(OH)2  2 CaCO3 ↓ + H2O (pH=9.25)
  Mg(HCO3)2 + Ca(OH)2  2 CaCO3 ↓ + Mg(OH)2 ↓ + 2H2O
  Soda Ash Softening
  CaSO4 + Na2CO3  CaCO3 ↓ + Na2SO4
  CaCl2 + Na2CO3  CaCO3 ↓ + 2 NaCl
  Lime-Soda Ash Softening
  MgSO4 + Ca(OH)2 + Na2CO3  CaCO3 ↓ + Mg(OH)2 ↓ + NaCO3
  Re-carbonation
  Ca(OH)2 + CO2  CaCO3 ↓ + H2O
  CaCO3 + CO2 +H2O  Ca(HCO3)2

## Slide 5: Water Treatment 4. Softening (Cation-Exchange)
Hard water is passed through a filter bed containing cation-exchange media (resins) where Ca++ and Mg++ are absorbed on the media and an equivalent amount of Na+ is released into solution.
Note:
Resin: insoluble polymers containing fixed cations or anions capable of reversible exchange with mobile ions in the solution with which they are brought into contact.
When the media is exhausted, a strong sodium chloride solution (NaCl) is passed through the bed to regenerate the media with Na+.
Softening
Ca++ CaR
+ Na R (Resin)  + Na+
Mg++ MgR
Regeneration
Ca R Ca++
+ NaCl  Na R +
Mg R Mg++

## Slide 6: Water Treatment 4. Softening (Cation-Exchange)
Example
For the water with the following chemical analysis to be softened by the cation-exchange process to zero hardness, sketch the meq/L bar graph of the softened water.
s
Ca++ | Mg++ | Na+
HCO3- | SO4-- | Cl-
0
4
7.5
6
0
5.3
7.5
6.2
Na+
HCO3- | SO4-- | Cl-
0
7.5
0
5.3
7.5
6.2

## Slide 7: Water Treatment 4. Softening (Cation-Exchange)
Comparison between Chemical and Ion-Exchange Treatment | 
Large quantities of chemical sludge | Brine product
Hardness cannot be reduced to zero | Hardness can be reduced to zero
Economical | Alkalinity is not consumed
 | The softened water contains high level of Na+
 | Water must be free of turbidity, Fe, and Mn

## Slide 8: Water Treatment Iron and Manganese Removal
Aeration, sedimentation and filtration
  Aeration oxidize the soluble ferrous iron (Fe++) to insoluble ferric iron (Fe+++)
  High removal of Mn++ is not possible by this technique because manganese cannot be oxidized as easily as iron with plain aeration.
  Aerator: tray type aerator, water is distributed on top of a series of trays from which it drips down the stack.
  Other types of aerators: spray nozzles, diffused air.

## Slide 9: Water Treatment Iron and Manganese Removal
Aeration, Chemical Oxidation, Sedimentation and filtration.
  The common method for the removal of Fe and Mn from well water without softening.
  Aeration: to initiate oxidation of Fe++ and Mn++.
  Chemical oxidation (e.g. potassium permanganate KMnO4, chlorine): to oxide Fe++ and Mn++:
  Fe(HCO3)2 + KMnO4  Fe(OH)3 ↓ + MnO2 ↓
  Ferrous bicarbonate Ferric hydroxide Manganese dioxide
  Mn(HCO3)2 + KMnO4  MnO2 ↓
  Manganous bicarbonate Manganese dioxide
  Theoretically, 1 mg/L of potassium permanganate oxidizes 1.06 mg/L of iron and 0.52 mg/L of manganese

## Slide 10: Water Treatment Iron and Manganese Removal
Example
  A well water supply contains 3.2 mg/L of iron and 0.8 mg/L of manganese. Estimate the dosage of potassium permanganate required for the iron and manganese oxidation.
  KMnO4 required = 3.2 x (1.0/1.06) + 0.8 x (1.0/0.52) = 3.02 + 1.54 = 4.6 mg/L

## Slide 11: Water Treatment Taste and Odor Control
Causes of Taste and Odor
  Ground water: dissolved gases (e.g. H2S, volatile organics, salts, metals such as Fe)
  Surface water: decayed vegetation (organics), algae, industrial wastes.
Measures for the control of taste and odor
  Prevention measures:
    Use of algicide to control of algae in surface water (e.g. copper sulfate).
    Maintain a proper pH (not less than 6.5) in water distribution systems to control the dissolution of copper and iron in water.
    Control discharges of industrial wastewater.
  Treatment measures:
    Aeration: to remove dissolved gases and volatile compounds.
    Oxidation methods: use of oxidants (e.g. chlorine, KMnO4, ozone)
    Carbon adsorption: use of activated carbon (expensive).

## Slide 12: Water Treatment Removal of Dissolved Salts (Desalinization)
Processes used for desalinization/demineralization:
Distillation – Reverse Osmosis – Ion Exchange – Electrodialysis
Salinity of seawater = 35000 mg/L (mostly sodium chloride)
Salinity of brackish groundwater > 1000 mg/L
Reverse Osmosis
  Osmosis: the process of diffusion/transfer of solvent (water) through a semi-permeable membrane from a solution of a lower to one of a higher concentration.
  Reverse Osmosis: the forced passage of water through a semi-permeable membrane against the natural osmotic pressure to accomplish separation of water and ions.

## Slide 13: Water Treatment Removal of Dissolved Salts (Desalinization)
Membranes:
  100 – 150 microns (skin layer < 1 micron + porous support structure)
  Size of pores : 0.001 microns (theoretical).
  Membrane material: cellulose acetate, polyamide.
  Membrane configuration/modules:
    Spiral-wound module
    d

## Slide 14: Water Treatment Removal of Dissolved Salts (Desalinization)
Membranes:
  Membrane configuration/modules:
    Hollow fiber module
      Outside diameter of hollow fibers = 80 – 100 microns
      Inside diameter = 40 microns

## Slide 15: Water Treatment Removal of Dissolved Salts (Desalinization)
Operation pressure of RO systems: 350 – 1500 psi (24 – 1200 bar)
  Note: Osmotic pressure of seawater = 350 psi
  Osmotic pressure of groundwater is much less (because TDS is low)
Pretreatment
  Saline water fed to RO system must be free of SS, organic matter, excessive hardness, and Fe and Mn to prevent fouling and scaling of membranes.
  Pre-treatment Methods:
    Coagulation and filtration: to remove turbidity, Fe and Mn.
    Softening: to remove hardness
    Adsorption (by AC): to remove organics.
    Acidification (addition of H2SO4): to reduce pH to less than 6 to convert HCO3- to CO2 gas in order to reduce CaCO3 scale and oxidation of Fe and Mn.
    Addition of scale inhibitors (e.g. hexametaphosphate): to prevent chemical scaling.

## Slide 16: Water Treatment Removal of Dissolved Salts (Desalinization)
Post-treatment
  Ro product (permeate) must be stabilized.
  Post-treatment methods:
    Aeration: to remove CO2.
    Addition of lime and soda ash: to adjust pH to about 8.0.
Membrane Cleaning
  Flushing with acid rinses and cleaning agents to remove buildup of salts, metal ions, organic matter, or biological growths.
Reject Brine
  Reject Brine = 10 % to 30 % of the feed water.
  s

## Slide 17: Water Treatment Disinfection
Purpose of disinfecting drinking water: to kill micro-organisms that cause diseases in humans (pathogens).
Disinfectants:
  Chlorine, Cl2  Chlorination
  Calcium hypochlorite, Ca(OCl)2  Chlorination
  Sodium hypochlorite, NaOCl  Chlorination
  Chlorine dioxide, ClO2  Chlorination
  Ozone, O3  Ozonation.
  Ultraviolet radiation (UV)  Disinfection with UV.
Treatment processes assist in removing pathogens
  Coagulation, settling, and filtration (over 90% removal is achieved).
  Excess-lime softening (due to high pH involved).

## Slide 18: Water Treatment Disinfection (1. Chlorination)
Chlorine is added to water in form of:
  Chlorine gas (Cl2): a greenish-yellow-colored, toxic gas. (supplied as liquefied gas in cylinder)
  Salts:
    Calcium hypochlorite, Ca(OCl)2 (available in powdered, granular, pellet, or tablet forms used in swimming pool and small treatment plants, that contain about 70 % chlorine)
    Sodium hypochlorite, NaOCl (available in liquid form at concentrations between 12 % and 15 % chlorine)

## Slide 19: Water Treatment Disinfection (1. Chlorination)
Chemistry of Chlorine
  Chlorine Reactions in Water
    Cl2 combines with water forming hypochlorous acid (HOCl):
    Cl2 + H2O  HOCl + H+ + Cl-
    HOCl ionizes into H+ and hypochlorite ion (OCl-) in a reversible reaction:
    ------- pH > 7.5 ------>
    HOCl OCl- + H+
    <----- pH < 7.5 -------
    Also calcium/sodium hypochlorites hydrolyze forming the hypochlorite ion (OCl-)
    Ca(OCl)2 + H2O  2 OCl- + Ca++ + H2O
    The killing efficiency of HOCl is about 40 to 80 times more than that of OCl-.
    Therefore, chlorination is more effective at low pH because HOCl is more dominant.
    Chlorine existing in water as HOCl and OCl- is called “free available chlorine”

## Slide 20: Water Treatment Disinfection (1. Chlorination)
Chlorine reactions with Ammonia
  Chlorine reacts with ammonia in water to form chloramines:
  HOCl + NH3  H2O + NH2Cl (mono-chloramine) at a pH 4.5 – 8.5 and > 8.5
  HOCl + NH2Cl  H2O + NHCl2 (di-chloramine) at pH 4.5 – 8.5
  HOCl + NHCl2  H2O + NCl3 (tri-chloramine) at pH < 4.4
  Chlorine in the form chloramines is called “combined available chlorine”.
  The addition of ammonia to chlorinated water to produce chloramines is called “chloramination”.
  Chloramines are effective for disinfection but to a lesser degree than free available chlorine.

## Slide 21: Water Treatment Disinfection (1. Chlorination)
Chlorine reactions with substances in water
  When chlorine is added to water (dosages up to 1 mg/L according to the Figure shown below), it oxidizes any present compounds (reducing compounds: inorganic such as Fe++, Mn++, H2S and NH3 and organics) and is converted to chloride ion. And thus, it is totally consumed and no residual appears (point A).
  If the initial dosage is higher (1 mg/L < dosage < 5 mg/L), chlorine reacts with ammonia to form chloramines, and reacts with organics to form chloro-organics. These products are called “combined chlorine residual” (points A and B).
  As the chlorine dosage is increased further (point B to point C) some of the chloramines and chloro-organics are destroyed (to form N2, nitrous N2O) and thus the combined residual is reduced.
  At point C, the combined residual reaches its lowest point (Point C is called the breakpoint).
  Dosages in excess of point C, produce “free chlorine residuals” [“free” in the sense that it has not reacted with anything, and “available” in the sense that it can react if necessary].
  The addition of chlorine to reach the breakpoint is called “breakpoint chlorination”.

## Slide 22: Water Treatment Disinfection (1. Chlorination)

## Slide 23: Water Treatment Disinfection (1. Chlorination)
Disinfection By-Products (DBPs)
  Chlorination of water containing natural humic organic substances produces toxic, carcinogenic chlorinated by-products:
    Trihalomethanes, THMs (e.g. chloroform, CHCl3, and bromodi-chloromethanes, CHBrCl2).
    Haloacetic acids, HAAs.
Control of Disinfection By-Products
  Reduce the formation of DBPs by applying chlorine to later stages of treatment (e.g. after filtration) in order to remove humic organics before chlorination.
  Application of activated carbon to absorb organics prior to chlorination.
  Use of alternative disinfectants that do not form these DBPs (e.g. chloramines, ozone).

## Slide 24: Water Treatment Disinfection (1. Chlorination)
Factors affecting the action of Chlorination
  Dosage and contact time.
  Tests must be done to determine the proper dosage of chlorine.
  Sufficient contact time must be ensured to kill microorganisms (at least 30 minutes) depending on the temperature and pH.
Examples

## Slide 25: Water Treatment Disinfection (2. Ozonation)
O3 decomposes in water to produce oxygen and free hydroxyl radicals (HO and HO2).
Very strong oxidant (more effective than chlorine)
Leaves no taste or odor
No residual is produced to protect water during distribution and transfer.
Must be generated on site because it decays rapidly.
More costly than chlorination.
Ozone forms carcinogenic and toxic DBPs such as aldehydes (e.g. formaldehyde), various acids (e.g. acetic acid), and brominated byproducts in the presence of bromide (e.g. bromate ion, bromoform, brominated acetic acids), and others.