## Slide 1: Sterile Products Lab PHT 434
Sterile Area

## Slide 2: Definitions
Sterilization: refers to any process that effectively kills or eliminates living microorganisms. It is not absolute. It is acceptable when it achieves killing effect of 10-6 i.e. every 1 million sterile items have a chance for only 1 item to be non-sterile.
Clean room: has a controlled level of contamination that is specified by the number of particles per cubic meter at a specified particle size.
Laminar flow: An airflow moving in a single direction and in parallel layers at constant velocity from the beginning to the end of a straight line vector.

## Slide 3: Definitions
HEBA filters: High Efficiency Particulate Air: remove at least 99.97% of airborne particles 0.3 µm in diameter.
ULPA filters: Ultra Low Particulate Air: remove at least 99.999% of airborne particles 0.12 µm in diameter.
Airlock: A small room with interlocked doors, constructed to maintain air pressure control between adjoining rooms (generally with different air cleanliness standards).

## Slide 4: Definitions
Bioburden: The total number of microorganisms associated with a specific item prior to sterilization.
Colony Forming Unit (CFU): A microbiological term that describes the formation of a single macroscopic colony after the introduction of one or more microorganisms to microbiological growth media. One colony forming unit is expressed as 1 CFU.
Endotoxin: A pyrogenic product (e.g., lipopolysaccharide) present in the bacterial cell wall. Endotoxin can lead to reactions in patients receiving injections ranging from fever to death.

## Slide 5: Methods of sterilization:
Terminal sterilization
  The product, container, and closure have low bioburden, but they are not sterile.
  The product in its final container is then subjected to a sterilization process such as heat or irradiation.
Aseptic conditions
  The drug product, container, and closure are first subjected to sterilization methods separately, as appropriate, and then brought together.

## Slide 6: Buildings and Facilities Clean rooms classification systems
Three classification system:
1- US Federal Standard 209E
  Measuring unit: max particles/ft3
  Class 100, 1000, 10000, 100000
  Class 100 means: not more than 100 particles of size ≥0.5 m present in one ft3
2- ISO 14644-1
  Measuring unit: max particles/m3
  Class ISO 5, ISO 6, ISO 7, ISO8
  Class ISO 5 means: not more than 3500 particles of size ≥ 0.5 m present in one m3
3- European GMP:
  Measuring unit: max particles/m3
  Class A, B, C, D
  Class A means: not more than 3500 particles of size ≥ 0.5 m present in one m3

## Slide 7: Buildings and Facilities Clean rooms classification systems
As 1m ≈ 35 ft, in the 3 classification systems:
  Class 100 = ISO 5 = Class A
  Class 1000 = ISO 6 = Class B
  Class 10,000 = ISO 7 = Class C
  Class 100,000 = ISO 8 = Class D
Class 100 = ISO 5 = Class A: contain less than 1 CFU/m3 (CFU/ft3)

## Slide 8: Buildings and Facilities Critical Area (class 100) (ISO 5) (Class A)
Operations:
  1- Sterile ingredients additions
  2- filling
  3- closure

## Slide 9: Buildings and Facilities Supporting Clean Areas
Function as zones in which non-sterile components, formulated products, in-process materials, equipment, and container/closures are prepared, held, or transferred.
FDA recommends that the area immediately adjacent to the aseptic processing line meet, at a minimum, Class 10,000 (ISO 7) standards.
An area classified at a Class 100,000 (ISO 8) is appropriate for less critical activities (e.g., equipment cleaning).

## Slide 10: Buildings and Facilities Clean Area Separation
1- Positive pressure differential between rooms of different classes.
2- Use of a double-door, airlocks or integrated sterilizer helps ensure direct product flow, often from a lower to a higher classified area.

## Slide 11: Buildings and Facilities Air Filtration
Class A:
HEPA-filtered air should be supplied at
  a velocity sufficient to sweep particles away from the filling/closing area
  maintain unidirectional airflow during operations

## Slide 12: Buildings and Facilities Air Filtration
Class A:
Membrane filters can be used to filter a compressed gas to meet an appropriate high-quality standard.
These filters are often used to produce a sterile compressed gas to conduct operations involving sterile materials, such as components and equipment

## Slide 13: Buildings and Facilities Design
Aseptic processes are designed to minimize exposure of sterile articles to the potential contamination hazards of the manufacturing operation.
Both personnel and material flow should be optimized to prevent unnecessary activities that could increase the potential for introducing contaminants to exposed product, container-closures, or the surrounding environment.

## Slide 14: Buildings and Facilities Changing room
Changing rooms leading into class A and B environment should be designed as airlocks.
There should be physical separation of the different stages of changing to minimize microbial and particulate contamination of clean room clothing.
Changing rooms for all classes should be flushed effectively with filtered air.

## Slide 15: Buildings and Facilities Changing room
The final stage of the changing room should be the same grade as the area into which it leads.
The use of separate changing rooms for entering and leaving clean areas is sometimes desirable.
In general, hand washing facilities should be provided only in the first stage of the changing rooms.

## Slide 16: Equipments
should be appropriately designed to facilitate ease of sterilization.
should not obstruct airflow and, in critical areas, its design should not disturb unidirectional airflow.

## Slide 17: Personnel
cGMP training
Gowning:
    Sterilized
    Non- shedding
    cover skin and hair (face-masks, hoods, beard/moustache covers, protective goggles, and elastic gloves are examples of common elements of gowns )
Keep the entire body out of the path of unidirectional airflow

## Slide 18: Personnel
  Keep the entire body out of the path of unidirectional airflow
  Number of personnel per area

## Slide 19: Components, containers, closures
It is important to characterize the microbial content (e.g., bioburden, endotoxin) of each component that could be contaminated and establish appropriate acceptance limits.
Pre-sterilization preparation of glass containers usually involves a series of wash and rinse cycles. These cycles serve an important role in removing foreign matter.
They should be subjected to sterilization and depyrogenation processes.

## Slide 20: New features
Blow/fill/seal technology
Blow/fill/seal units are purpose built machines in which, in one continuous operation,
  containers are formed from a thermoplastic granulate,
  filled with the sterile formulation
  and then sealed.
all by the one automatic machine.