## Slide 1: CE 445 Wastewater Reclamation and Reuse
Dr. Mohab Kamal

## Slide 2: Introduction to Stabilization
Solids and bio-solids are stabilized to (1) reduce pathogens, (2) eliminate offensive odors, and (3) inhibit, reduce, or eliminate the potential for decomposition.

## Slide 3: Description of Stabilization Processes

## Slide 6: Conditioning
Sludge and biosolids are chemically conditioned expressly to improve their dewatering characteristics. Other conditioning methods, heat treatment and freeze-thaw, have also been used to a limited extent.
Chemical Conditioning
The use of chemicals to condition sludge and biosolids for dewatering is economoical because of the increased yields and greater flexibility obtained. Chemical conditioning can reduce the 90 to 99 percent incoming moisture to 65 to 85 percent, depending on the nature of the solids to be treated.
Chemicals used include ferric chloride, lime, alum and organic polymers.

## Slide 7: Dewatering
Dewatering is a physical unit operation used to reduce the moisture content of sludge and biosolids for one or more of the following reasons:
Reduce the cost of trucking sludge and biosolids.
Dewater sludge are generally easier to handle than thickened or liquid sludge.
Dewatering is required prior to the incineration of the sludge.
Dewatering is required before composting.
To render biosolids odorless and no putrescible.
Dewatering is required prior to landfilling sludge.
Several techniques are used in dewatering devices for removing moisture. The dewatering processes that are commonly used include centrifuges, belt-filter presses, recessed-plate filter presses, drying beds, and lagoons.

## Slide 8: Heat Drying
Heat drying involves the application of heat to evaporate water and to reduce the moisture content of biosolids below that achievable by conventional dewatering methods.
The classification of dryers is based on the predominant method of transferring heat to wet solids. These methods are convection, conduction, radiation, or a combination of both.

## Slide 9: Incineration
Incineration of sludge involves the total conversion of organic solids to oxidized end products, primarily carbon dioxide, water, and ash.
The major advantages of incineration are:
1. maximum volume reduction
2. destruction of pathogens and toxic compounds and
3. energy recovery potential.
Disadvantages include
1. high capital and operating cost
2. highly skilled operating and maintenance staff
3. the residuals produced may have adverse environmental effects
4. disposal of residuals, which may be classified as hazardous wastes.

## Slide 10: Application of Biosolids to Land
Land application of biosolids is defined as the spreading of biosolids on or just below the soil surface.
Biosolids may be applied to
  Agricultural land
  Forest land,
  Disturbed land, and
  Dedicated land disposal sites