## Slide 1: CE 445 Wastewater Reclamation and Reuse
Dr. Mohab Kamal

## Slide 2: Activated Carbon
In water reclamation, adsorption processes are sometimes used to remove dissolved constituents by accumulation on a solid phase.
Activated carbon is a common adsorbent, which is employed as powdered activated carbon (PAC) with a grain diameter of less than 0.074 mm or granular activated carbon (GAC), which has a particle diameter greater than 0.1 mm.
During water reclamation, PAC can be added directly to the activated sludge process or solids contact processes, upstream of a tertiary filtration step.
GAC is used in pressure and gravity filtration.

## Slide 3: Activated Carbon
Activated carbon is efficient for the removal of many regulated synthetic organic compounds as well as unregulated trace organic chemicals exhibiting properties of high and moderate hydrophobicity (e.g., steroid hormones, triclosan, bisphenol A) (Snyder et al., 2006a).
Although PAC needs to be disposed of after its adsorption capacity is reached, GAC can be regenerated either on- or offsite, providing this practice is more cost-effective than disposing it via landfills.
Onsite GAC regeneration is only cost-effective for large installations and is currently not practiced by any water reclamation facility in the United States.
GAC adsorbents are characterized by short empty-bed contact times (i.e., 5-30 min) and preferably a large throughput volume (i.e., bed volumes of 2,000 to 20,000 m3/m3)

## Slide 4: Biological Filtration
For instance, simple aldehydes, ketones, and carboxylic acids are produced as ozone oxidizes organic matter in water.
The aggregate measurements commonly employed to assess the biodegradability of transformation products is assimilable organic carbon (AOC) (Hammes and Egli, 2005) and biodegradable dissolved organic carbon (BDOC) (Servais et al., 1987).
This readily biodegradable carbon has been implicated in the acceleration and promotion of biofilm growth in distribution systems.
Thus, drinking water treatment facilities usually employ biofiltration after ozonation to reduce BDOC with the aid of indigenous bacteria present in the feedwater.
Additionally, the use of biofiltration after ozone also has been shown to reduce the formation of some byproducts formed during secondary disinfection with chlorine (Wert et al., 2007).
Some studies have also demonstrated that the byproducts from ozonation of trace organic chemicals, such as steroid hormones and pharmaceuticals, also are largely biodegradable (Stalter et al., 2010); therefore, there is growing support for the use of biofiltration after ozone or AOP.
Although biofiltration alone may provide some direct benefit in terms of removing trace organic chemicals, it has generally been shown to be only marginally effective without a prior oxidation step (Juhna and Melin, 2006).

## Slide 5: Biological Filtration
Biological filtration can be accomplished using traditional media (i.e., sand/anthracite) or using activated carbon (biologically activated carbon [BAC]).
Although some studies have suggested that activated carbon is superior for supporting biological growth, mainly because of superior adherence of the biofilm to the GAC, there are some conflicting reports that show approximately equal performance using anthracite (Wert et al., 2008).
Some studies have demonstrated that BAC is capable of adsorption as well as biological degradation; however, the adsorptive capacity of the BAC will eventually be reduced as the micro-pores in the carbon structure become blocked and the adsorptive capacity subsequently becomes exhausted.

## Slide 6: Biological Filtration
Some studies have demonstrated that BAC is capable of adsorption as well as biological degradation; however, the adsorptive capacity of the BAC will eventually be reduced as the micro-pores in the carbon structure become blocked and the adsorptive capacity subsequently becomes exhausted.
At this point, fresh GAC will be required to restore the adsorptive capacity, but effective biological activity as measured by reduction of AOC or BDOC will take time to establish.
The amount of time needed to develop a biologically active filter will depend on water quality, water temperature, and operational parameters.
An important factor in establishing and maintaining an active biofilm is the backwash frequency with chlorinated water.

## Slide 7: Biological Filtration
One major disadvantage of using biological filtration is the detachment of biofilm and likely detection of bacteria in filtered water.
Although these bacteria are not harmful, the detection of heterotrophic bacteria could in some cases lead to regulatory violations. In those cases, biofiltration would generally be followed by a disinfection step, such as chlorination or UV irradiation.

## Slide 8: Chemical Oxidation
Chemical oxidation is commonly employed in water treatment to achieve disinfection, as described previously in this chapter; however, oxidants are also used to remove tastes, odors, and color and to improve the removal of metals (Singer and Reckhow, 2010).
Oxidants used for water treatment include chlorine, chloramine, ozone, permanganate, chlorine dioxide, and ferrate.
Advanced oxidation relies upon formation of powerful radical species, primarily hydroxyl radicals (OH·) and is rapidly gaining in use for the oxidation of more resistant chemicals, such as many trace organic chemicals and industrial solvents (Esplugas et al., 2007).
The most commonly employed advanced oxidation techniques in water reclamation use hydrogen peroxide coupled with UV light or ozone gas.
The UV light itself is not strictly an oxidant but it does selectively transform a small group of compounds sensitive to direct photolysis (e.g., NDMA, iohexol, triclosan, acetaminophen, diclofenac, sulfamethoxazole) (Pereira et al., 2007; Snyder et al., 2007; Yuan et al., 2009; and Sanches et al., 2010).

## Slide 9: Chemical Oxidation
Very few oxidative technologies are employed at operational conditions capable of mineralizing organic materials in water.
Even the most promising advanced oxidation techniques using ozone and UV irradiation combined with peroxide will result in only a minor (if any) measurable reduction of dissolved organic carbon (DOC).
Regardless of the oxidation technique deployed and superior performance of trace organic chemical removal, some transformation products will result that are often uncharacterized.
The most commonly used oxidation methods for the removal of trace organic contaminants are described below.

## Slide 10: Chemical Oxidation Chlorine
Chlorine, defined here as the combination of chlorine gas, HOCl, and OCl–, reacts selectively with electron-rich bonds of organic chemicals (e.g., double bonds in aromatic hydrocarbons) (Minear and Amy, 1996).
Recently, several reports have shown that many trace organic chemicals containing reactive functional groups can be oxidized by free chlorine (Adams et al., 2002; Deborde et al., 2004; Lee et al., 2004, Pinkston and Sedlak, 2004; Westerhoff et al., 2005), while ketone steroids (e.g., testosterone and progesterone) are not as effectively oxidized (Westerhoff et al., 2005).
However, the ability of chlorine to effectively oxidize trace organic chemicals, including steroid hormones, is a function of contact time and dose.
More importantly, chlorine is not expected to mineralize trace organic chemicals, but rather to transform them into new products (Vanderford et al., 2008), which may in fact be more toxic than the original molecule.

## Slide 11: Chemical Oxidation Chloramines
Chloramines are not nearly as effective as oxidants and thus play a much smaller role in trace organic chemical oxidation.
Snyder (2007) demonstrated that a dose of 3 mg/L chloramines and a contact time of 24 hours was able to effectively oxidize phenolic steroid hormones (e.g., estrone, estradiol, estriol, ethinyl estradiol) as well as triclosan and acetaminophen; however, the vast majority of trace organic chemicals studied were not significant oxidized.
Therefore, although chloramines play an important role in reduction of membrane fouling and disinfection, only minimal expected benefit in oxidation of trace organic chemicals will result.
Moreover, careful evaluation of nitrosamine formation should be undertaken when using chloramines, considering the carcinogenic potency of these byproducts (see Choi et al., 2002; Mitch et al., 2003; Haas, 2010).

## Slide 12: Chemical Oxidation Ozone
Ozone (O3) is a powerful oxidant and disinfectant that decays rapidly and leaves no appreciable residual in reclaimed water during storage and distribution.
Ozone-enriched oxygen is generally added to water through diffusers producing fine bubbles, and once dissolved in water, ozone quickly undergoes a cascade of reactions, including decomposition into hydroxyl radicals (OH·), hydroperoxyl radical (HO2), and superoxide ion (O2–).
These radicals along with molecular ozone will rapidly react with organic matter, carbonate, bicarbonate, reduced metals, and other constituents in water.
The reactions mediated by the hydroxyl radical are relatively nonselective, whereas molecular ozone is more selective (Elovitz et al., 2000).

## Slide 13: Chemical Oxidation Ozone
Because of ozone’s ability to oxidize organic chemicals, it has been widely applied in water treatment for taste and odor control, color removal, and to reduce concentrations of trace organic chemicals.
At dosages commonly employed for disinfection, the vast majority of contaminants can be effectively converted into transformation products (Snyder et al., 2006c).
Although several studies have shown that ozone effectively reduces estrogenic potency in reclaimed water (Snyder et al., 2006c), recent publications have suggested that biologically active filters be included after the ozone process in order to remove biodegradable byproducts formed during ozonation (Stalter et al., 2010).
For potable reuse applications, ozonation could also be applied after soil aquifer treatment (SAT), which combines the benefits of a more selective oxidation of remaining chemicals persistent to biodegradation and a lower ozone demand due to reduced DOC concentrations in the recovered water.

## Slide 14: Chemical Oxidation Ozone
It is well known that in the presence of bromide, ozone can form bromate, a toxic byproduct. There are steps that can be employed to mitigate the formation of bromate, such as the use of chlorine and ammonia before ozone addition (von Gunten, 2003).
Some reports have shown that ozone applied before chloramination also results in the oxidation of nitrosamine precursors (Lee et al., 2007). However, ozone also has been shown to form some nitrosamines directly (von Gunten et al., 2010).

## Slide 15: Chemical Oxidation Ozone
Ozone can play an important role in water reclamation, but the process is more energy intensive and operationally complex than chlorination.
In cases where trace organic chemical removal (e.g., pharmaceuticals, steroid hormones) is important, ozone is a viable option and does not result in a residuals stream like NF or RO membrane processes or in spent media as with activated carbon.
However, ozone does not provide a complete barrier to trace organic chemicals, and there are certain chemicals that are not amendable to oxidation (e.g., chlorinated flame retardants; artificial sweeteners) (Snyder et al., 2006c).

## Slide 16: Chemical Oxidation UV Radiation
UV light at doses commonly employed for disinfection (40–80 mJ/cm2) is largely ineffective for trace organic chemical removal.
In a recent study that investigated the removal of trace organic chemicals from water, none of the target compounds investigated were well removed (>80 percent oxidized) using UV at disinfection doses (Snyder, 2007).
However, when UV doses are significantly increased (generally by 10-fold) and high doses of hydrogen peroxide (5 mg/L and higher) are added, most trace organic chemicals were effectively oxidized (Snyder et al., 2006c).
Activated carbon is sometimes employed to catalytically remove hydrogen peroxide, and other chemicals can be used to remove excess peroxide from the UV-AOP effluent.

## Slide 17: Chemical Oxidation UV Radiation
Although UV-AOP does form transformation products (i.e., it does not result in mineralization of organic compounds), it does not form bromate.
Additionally, UV alone at elevated dosages or in combination with hydrogen peroxide (UV-AOP) effectively removes NDMA.
UV-AOP efficacy, however, is quite susceptible to water quality and requires proper pretreatment.
In many potable reuse applications, UV-AOP is applied after RO treatment to negate the detrimental impacts of water quality, such as suspended and particulate matter and DOC.
UV-AOP applications generally will require extensive pretreatment to increase UV transmittance; however, recent studies have demonstrated that UV-AOP can be also effective in advanced-treated effluents (Rosario-Ortiz et al., 2010).