## Slide 1: CE 445 Wastewater Reclamation and Reuse
Dr. Mohab Kamal

## Slide 2: Reducing Fresh Water Usage
Before considering the reuse of rainwater and greywater, the most basic strategy to reduce potable water consumption is to use low-flow or high efficiency fixtures and appliances wherever possible.
These may include shower heads, restroom or kitchen faucets, toilets, urinals, water fountains, dishwashers, washers, cooling systems, and landscape irrigation systems.

## Slide 3: Reducing Fresh Water Usage
Accepted Toilet/Urinal Strategies
  High efficiency toilets (HETs): High efficiency toilets have been defined by the EPA as using, on average, 20% less water per flush than the industry-accepted standard of 1.6 gallons per flush-around 1.28 gallons per flush maximum. Utilizing HETs can significantly reduce the amount of potable water demand, particularly if more innovative water-saving toilets are used.
  Dual flush toilets: Dual flush toilets are commonly used in Europe and Australia and are gaining popularity in the US as well. A dual flush toilet has two flushing options: a 0.8 gallon flush for urine only or a 1.6 gallon full tank flush for solid waste. The 2 options are typically displayed as two buttons or a variant on a handle. The handle either goes up for one flushing option and down for the other option, or a smaller handle (for the 0.8 gallon flush) is included in addition to the regularly sized handle.

## Slide 4: Reducing Fresh Water Usage
Other Toilet/Urinal Strategies
  Waterless urinals: Waterless urinals have been implemented locally over the past several years, as test cases, with mixed results. One cause for failure has been the corrosion of copper piping that drains the urinals.
  Composting toilet: A traditional composting toilet consists of an aerobic processing system that treats human waste with little or no water involved. This is either accomplished through composting or managed aerobic decomposition.
Accepted Toilet/Urinal Strategies
  High efficiency urinals (HEUs): High efficiency urinals use on average 0.5 gallons per flush or less, which is at least half the water used to flush a traditional urinal. Several HEUs now on the market, use just a pint of water per flush, and have been found to outperform waterless urinals and perform similarly to traditional urinals.

## Slide 5: Rainwater Harvesting System Design
Rainwater harvesting systems can be utilized at an exterior and/or interior building level for irrigation or toilet or urinal flushing or for other nonpotable uses, as a way to drastically reduce potable water use, help manage stormwater, and enhance the environmental sensitivity of buildings.
The basic strategy for such interior systems is to harvest rain from roof catchment surfaces, filter and purify the water to an acceptable water quality standard, and store it until needed to flush toilets and/or urinals.
Utilizing a rainwater harvesting system can make a huge impact in terms of water conservation, particularly for office and institutional buildings where flush fixtures may be a major part of the demand for potable water.

## Slide 6: Rainwater Harvesting System Design
There are many options for system design. The basic components of a water reuse system, as illustrated on the Sample Rainwater Harvesting System Diagram include a water source, filtration component, purification strategies, delivery method, and an end use. Typical options for each component are given in the following text; however, options unique to each project should be pursued as necessary. The specifics of each system will vary based on size and use.

## Slide 7: Rainwater Harvesting System Design Design Components 1. START: Rainwater Catchment (roof)
Potential sources: Several sources of water may be appropriate for use in a rainwater harvesting system, including rainwater from a roof catchment, groundwater, or condensate. Each source has a different set of design requirements, as outlined below. This manual will focus on rainwater catchment from roof sources.
Roof catchment:
  Capturing rainwater from a roof surface is a common method of obtaining water for a rainwater harvesting system.
  Smoother surfaces, such as metal or slate, are best for maximizing the amount of rainwater captured.
  Other materials, such as clay, concrete, or composite or asphalt shingles, may create inefficiencies, losing up to 10% of rainwater due to their texture, inefficient flow, and/or evaporation.
  Wood shingles, tar, and gravel roofs should be avoided for rainwater harvesting systems where water is reused to flush toilets or urinals to avoid unnecessary debris and pollutants in the water.
  Gutter and downspouts are necessary to direct rainwater into the filtration system.
  Gutters and downspouts are typically comprised of half-round pvc, vinyl, seamless aluminum, or galvanized steel.

## Slide 8: Rainwater Harvesting System Design Design Components 1. START: Rainwater Catchment (roof)
Condensate:
  Condensate from the cooling coils of an air conditioning system is a relatively clean source for a water harvesting system, with the exception of glycol/chemical systems. Such systems are more suitable for condensate make-up than for other uses, due to possible chemical/glycol leakage.
  Capturing condensate for reuse for a commercial or institutional building can result in millions of gallons of water saved during the course of a cooling season.
  Harvesting condensate is typically a simple process requiring the redirection of the condensate (via a rerouted waste line or addition of a discharge pit and pump) to the rainwater harvesting system to be filtered and purified.

## Slide 9: Rainwater Harvesting System Design Design Components 1. START: Rainwater Catchment (roof)
Rainwater collected at ground level and Groundwater:
  Provided such rainwater is not contaminated by parking lot residues, runoff pollutants, etc., rainwater collected at ground level is also a great source for rainwater harvesting systems.
  Currently such systems, as well as groundwater systems require IDPH test site approval.
  They may be allowed on a case-by-case basis, and typically require pre-treatment prior to collection. An initial filter may include mechanical or natural filtration processes, such as sand, sediment, or geotextile fabric, as well as organic filtration (such as vegetated bioswales); often the wall of the sub-grade tank acts as the filter itself.
  Due to the volume of groundwater available to be harvested, storage in an underground tank is recommended; however, above ground cisterns may be used.
  Underground tanks should be constructed of materials such as reinforced polypropelene, fiberglass, or concrete that have sufficient strength under load-bearing surfaces.
  A sump pump may be needed to feed water into the rainwater harvesting system’s filter prior to purification; rainwater from the underground storage tank should be drawn as needed to support minimum water levels in the day tank.

## Slide 10: Rainwater Harvesting System Design Design Components 2. Initial Filtration/Diversion
Before the rainwater travels through the system, it is necessary to remove any leaves, twigs, blossoms, insect bodies, and other large objects from the rainwater to avoid clogging the system.
This is typically accomplished through the use of a leaf screen or vortex filter.
This filter can be located above or below ground and has to be cleaned out on a regular basis to avoid clogging.
Roof surfaces typically contain a variety of contaminants including dust, pollen, animal feces, pesticides and sediment.
The first flush diversion via a solenoid valve removes most of these contaminants by directing the first several minutes/gallons of the rainfall event to the sewer system instead of to the rainwater harvesting system.
First flush systems either designate a volume of rainwater to be diverted (# of gallons) or a preset amount of time to flush water (# of minutes).
Volumetric first flush diverters are more expensive than timed diverters with little proven benefit; therefore timed first flush diverters are recommended unless there is a compelling reason to use a volumetric diverter.

## Slide 11: Rainwater Harvesting System Design Design Components 2. Initial Filtration/Diversion
Solenoid valve:
  A solenoid valve is included to assist the first flush by directing the flow of rainwater to the sewer while the flush is occurring and switching over to channel rainwater to the rainwater harvesting system after the flush has occurred.
  The valve acts as a fail safe to divert rainwater to the sewer in the event of a problem with the system or if the tank is full.
  The solenoid valve should be located before the initial filter discussed below to avoid unnecessarily filtering water that will end up in the sewer system.

## Slide 12: Rainwater Harvesting System Design Design Components 3. Holding Tank
A storage tank is a larger scale tank designed to hold a large quantity of rainwater until it is sent for treatment within the rainwater harvesting system; such a tank may be an above-ground cistern or underground storage tank.
Smaller systems may just have one combined holding tank/day tank.
For water harvest systems used exterior to a building for irrigation only, water from the holding tank would be used directly.
If make-up from municipal water is required, an air gap will be necessary to avoid possible contamination.

## Slide 13: Rainwater Harvesting System Design Design Components 4. Filter
To further remove particulate matter and cloudiness, an in-line sediment filter or series of filters is recommended after the initial filter removes large impurities. These filters should remove particles larger than 25 microns.
If a UV purification system is used, a series of filters should filter the greywater to 1 micron prior to disinfection by the UV light.
The greywater must be filtered prior to exposure to the UV because suspended particles in the water can shield pathogens from disinfection.
The UV light should be located before the storage tank, although an additional UV light may be placed in the storage tank to continue disinfection.

## Slide 14: Rainwater Harvesting System Design Design Components 5. Purification System
One of the following options should be utilized to purify the harvested rainwater prior to its entry into the storage tank.
Chlorination: Chlorination as a method of purification in rainwater harvesting systems has been the top choice of local municipalities due to its reliability.
When chlorine is used to purify rainwater, residual chlorine remains, giving the rainwater lasting purification.
On the other hand, after rainwater passes by a UV light, there is no purification after the point of contact with the UV, potentially allowing bacteria to grow after contact with the UV.

## Slide 15: Rainwater Harvesting System Design Design Components 5. Purification System
Sufficient contact time with chlorine is critical to kill bacteria.
Contact time should be determined by considering water pH, temperature, and the amount of potential bacteria. The system should incorporate a fail-safe feature that reverts the system back to municipal make-up water if chlorine levels fall below the accepted standard.
Another potential drawback of using chlorine is that the smell of the chemical may be objectionable. The chemical itself also has negative environmental impacts, including the formation of trihalomethanes, which have been shown to cause several types of cancer.
Another consideration is that chlorine does not kill giardia or cryptosporidium, both of which can cause parasitic infection allowed to exist in potable water.
These two parasites may only be eliminated by a 1-micron filter or UV purification.

## Slide 16: Rainwater Harvesting System Design Design Components 5. Purification System
There are two major options to choose from if utilizing a chlorine based purification system.
  Liquid chlorine can be used as a drip to continuously adjust chlorine levels. Use of liquid chlorine may be more appropriate for uses with full-time maintenance staff, as it needs consistent monitoring and maintenance attention.
  Liquid chlorine is also more dangerous than dry chlorine tablets, making it more appropriate for trained staff to handle. Liquid chlorine should be handled with care, as chlorine that comes into contact with skin will cause a potentially severe freeze burn.
  Chlorine tablets, such as calcium hypochlorite briquettes, are the preferred option for chlorine purification systems.
  These are similar to what is used for large-scale water treatment facilities but are more user-friendly and safe for building maintenance staff (or residents) to handle.
  The tablets are combined with water in a hopper to create a liquid chlorine, which is then applied to the rainwater to achieve a satisfactory level.
  The tablets must be replenished; the frequency depends on the usage of the system. Use of briquettes or tablets is recommended for systems where a full-time maintenance staff is not employed.

## Slide 17: Rainwater Harvesting System Design Design Components 5. Purification System
Ultraviolet (UV) light:
  UV light is an accepted purification alternative to chlorine.
  A specific wavelength of UV light destroys any organisms present in the rainwater.
  Typically, UV purification consists of a series of in-line sediment filters which filter the rainwater to 1 micron prior to disinfection by the UV light.
  The rainwater must be filtered prior to exposure to the UV because suspended particles in the water can shield pathogens from disinfection.
  The UV light should be located before the storage tank, although an additional UV light may be placed in the storage tank to continue disinfection.
  As an alternative to having another UV light in the tank, rainwater may be recirculated past the UV light in order to provide continual disinfection; however, this may heat the water over time.
  UV purification systems have maintenance requirements as well.
  The UV bulb needs to be changed approximately once every 10,000 hours or after 12 months of continuous use; some bulbs come with an alarm that alerts occupants when the light quality is degrading.
  In addition, the sediment filters need to be replaced regularly.

## Slide 18: Rainwater Harvesting System Design Design Components 6. Day Tank
There are two major types of tanks that may be used within a rainwater harvesting system, depending on the design of the system and quantity of water desired to be collected--a holding tank and a day tank.
A day tank is smaller and meant to hold treated rainwater until it is needed for flushing.

## Slide 19: Rainwater Harvesting System Design Design Components 6. Day Tank
Sizes of the system’s tanks can be determined by several factors, including the demand for treated water, rainwater supply of the region, projected length of dry spells, catchment surface area, aesthetics, preference, and budget.
The size, location, and function of the tank should be considered in choosing the most appropriate material for the tank.
Common materials for storage tanks include concrete, polyethylene, fiberglass, polypropylene, or galvanized metal.
The tank must be opaque to protect against algae growth unless an agitator is included in the tank, in which case the tank may be semi-translucent.
Opaque tanks may incorporate a translucent strip or floating indicator to show tank water level. When locating the tank, consider the proximity of building foundations and the ability to drain the tank effectively.

## Slide 20: Rainwater Harvesting System Design Design Components 6. Day Tank
Municipal make-up water: In case the rainwater supply runs short of the demand for irrigation or toilet/urinal flushing, the rainwater harvesting system must incorporate a municipal make-up water supply to the storage tank that will initiate when tank level sensors determine that the water level in the tank is low. The municipal water source must be protected from backflow contamination by incorporating a fixed air gap.
Overflow drain: If the storage tank becomes too full, an overflow drain should be incorporated to funnel excess water to the sewer through means of an indirect connection. A u-trap and rodent guard should be placed in the overflow drain to protect the supply from gasses and prevent rodents from climbing back into the storage tank and contaminating the harvested water supply.

## Slide 21: Rainwater Harvesting System Design Design Components 6. Day Tank
Ventilation: When chlorination is utilized as a purification method, it is necessary to ventilate the tank room to the outdoors to remove any fumes that might occur. All storage tanks must be vented regardless of the purification system used.
Water level sensors: The storage tank should contain 2 sensors: (1) to alert the control panel when the tank level is high and further rainwater is not needed (additional rainwater will be diverted to the sewer until water is needed for the system again) and (2) to alert the control panel when the tank level is low and municipal make-up water is needed.

## Slide 22: Rainwater Harvesting System Design Design Components 6. Day Tank
Control panel: A centralized control panel is critical for proper maintenance of the system and to bring immediate attention to a cross-contamination issue. It also may be a useful learning tool in the appropriate setting (such as in a public area of the building like a lobby). The control panel may display such items as:
  Volume of harvested rainwater
  Volume of municipal make-up water used
  Any loss in pressure and its location in the system, which may indicate that a filter needs to be cleaned or other maintenance is necessary
  Indicator light for UV system - when bulbs needs replacement or if there is a problem with the system
  Indicator light for chlorination system - if chlorine levels have fallen below accepted standards, if chlorine is needed, or If there is a problem with the system

## Slide 23: Rainwater Harvesting System Design Design Components 7. Booster Pump
When treated water is needed for flushing, it must be pressurized to get it to its destination. This is typically accomplished through the use of a booster pump after the water leaves the storage tank; however, this may not be necessary if gravity can be used to assist in moving the treated water.

## Slide 24: Rainwater Harvesting System Design Design Components 7. Booster Pump
When treated water is needed for flushing, it must be pressurized to get it to its destination. This is typically accomplished through the use of a booster pump after the water leaves the storage tank; however, this may not be necessary if gravity can be used to assist in moving the treated water.

## Slide 25: Rainwater Harvesting System Design Design Components 8. Finish: Flushing Toilets and Urinals
The distribution piping from the rainwater harvesting system must itself be permanently identified by a distinctive yellow-colored paint or purple pipe. The piping or insulation must be marked as “nonpotable” at intervals not to exceed ten feet.
In addition, each toilet or urinal supplied with harvested rainwater must be provided with a permanently affixed wall sign with yellow lettering stating, “This fixture is flushed with harvested rainwater.
Not safe for drinking,” or similar wording. To further discourage potable use, non-residential applications may dye the treated water blue or green with food grade vegetable dye.