## Slide 1: CE 445 Wastewater Reclamation and Reuse
Dr. Mohab Kamal

## Slide 2
The basic strategy of a greywater system for interior building reuse is to harvest greywater from appropriate sources (such as shower, lavatory, and laundry water), filter and purify the water to an acceptable water quality standard, and store it until needed to flush toilets and/or urinals.
Greywater reuse makes the most sense where an adequate source water is present and available to be harvested.
For example, a public restroom with only includes a few sinks and toilet/urinal fixtures and is likely not worth the expense of installing a greywater system when a rainwater harvesting system would be a better choice. Buildings that incorporate showers, such as fire stations or residential buildings, are good candidates for greywater systems as the water from one shower is approximately equal to one person’s flushing needs for a day. See Planning for a Greywater System for more information on choosing the proper system.
Greywater System Design

## Slide 3: Greywater System Design

## Slide 4
Several sources of water may be appropriate for use in a greywater system, including used water from showers, lavatories, or washing machines. Sources do not include water from the kitchen sink, dishwasher, or blackwater (wastewater from toilets and urinals).
Kitchen wastewater and blackwater contain high amounts of organic and inorganic contaminants and bacteria which should be avoided for greywater systems.
All greywater sources, especially laundry water, should avoid cleaners that contain harsh chemicals, bleaches, disinfectants, or phosphates.
Ammonia-based cleaners should not be used in washing machines contributing to a greywater system that uses chlorine purification, as such cleaners combined with chlorine may form chlorine gas.
Hazardous chemicals should never be put down a drain that contributes to a greywater system. In addition, washing machines used as a greywater source should not be used to wash heavily soiled or human waste-soiled items (i.e. dirty diapers).
Greywater System Design Design Components 1. Start: Greywater Source

## Slide 5
An initial filter serves to remove hair, lint, and other solids from the greywater source to reduce the risk of clogging the system downstream. Cleaning of this filter should occur regularly.
Greywater System Design Design Components 2. Initial Filter

## Slide 6
See the Rainwater Harvesting System discussion on filters.
The majority of information included there is also applicable to greywater systems, with the following clarifications.
Ultrafiltration and reverse osmosis filter water to a finer degree than particle filters and may be useful to include in a greywater system, due to various contaminants and particles that source water may contain.
These options should be explored during the design of the system.
Greywater System Design Design Components 3. Filter

## Slide 7: Greywater System Design Design Components 4. Purification System
See the Rainwater Harvesting System discussion on UV and chlorination purification techniques. The majority of information included there is also applicable to greywater systems, with the following clarifications.
Chlorine loop (applies only if chlorination is used for purification of greywater): Due to higher levels of impurities and pollutants in greywater, the system should incorporate a dosing loop to recirculate water in the storage tank through the purification system to maintain the desired chlorine level. As an alternative, an automatic chlorine analyzer can continuously monitor chlorine levels and provide more chlorine via a chemical injection pump if necessary. The system should incorporate a fail-safe feature that automatically reverts the system to municipal make-up water if chlorine levels fall below the acceptable level.

## Slide 8: Greywater System Design Design Components 4. Purification System
UV in storage tank: If UV purification is used, an additional UV light and water agitator should be placed in the storage tank to continue disinfection. As an alternative to placing another UV light in the tank, greywater may be recirculated past the UV light to provide continual disinfection; however, this may heat the water over time.
Ozone: Ozone, although not as widely used as the other two purification methods, may be used as an alternative to UV or chlorine disinfection. The greywater should be afforded adequate contact time with the ozone system. Provisions must be made to off-gas the ozone to a safe environment. In addition, since ozone is a hazardous and powerful treatment method, its use may be better suited for larger scale applications where maintenance staff is on-hand to monitor the system closely.

## Slide 9: Greywater System Design Design Components 4. Purification System
Ultra filtration: Due to the contaminants that may be present in greywater, one option is to include ultra filtration membranes as an alternative filtering mechanism. Ultra filtration is very effective in removing pathogens, bacteria, viruses, and other particulate matter to 0.02 microns or better (see chart on page 54). Ultra filtration is also more efficient than other methods of filtration, consistent in its results regardless of load, easy to manage, and, when combined with chlorine purification, will produce pathogen-free water.
Reverse osmosis: Reverse osmosis is a technique which can filter water to an even finer grain than ultra filtration, down to 0.001 microns or less. Reverse osmosis (RO) is similar to ultra filtration, although there are some key differences. It works by applying pressure to the solution when it is on one side of a selective membrane, forcing pure solution to filter through while unwanted molecules and ions stay behind.
Depending on the contaminants that may be present in the water to be reused, reverse osmosis may be considered as an alternative to sand filtration. An activated carbon filter may be needed to trap organic chemicals and chlorine, which will attack and degrade certain types of reverse osmosis membranes.

## Slide 10: Greywater System Design Design Components 5. Storage Tank
See the Rainwater Harvesting System discussion on storage tanks. The majority of information included there is also applicable to greywater systems, with the following clarifications.
The storage tank should contain 2 sensors: (1) to alert the control panel when the tank level is high and further greywater is not needed (additional greywater will be diverted to the sewer until greywater is needed for the system again) and (2) to alert the control panel when the tank level is low and municipal make-up water is needed.

## Slide 11: Greywater System Design Design Components 6. Booster Pump & 7. Finish: Flushing Toilets and Urinals
See the Rainwater Harvesting System discussion; this information is also applicable to greywater systems.

## Slide 12: Disinfection and Filtration Methods, Costs & Maintenance

## Slide 13: Blackwater Systems
Blackwater systems take wastewater from flush fixtures, typically containing fecal matter and urine, process it, and enable it to be reused for toilet flushing, irrigation, or fertilization of gardens or agriculture.
There are several different strategies that accomplish this purpose, which are outlined below.

## Slide 14: Blackwater Systems Aeration-Based Blackwater System
Aerated systems work by using accelerated aerobic and anaerobic decomposition to remove bacteria and particles from the blackwater.
Such systems typically have several key components:
  A septic tank providing an anaerobic bacterial environment to settle out and decompose large solids
  An aeration chamber where air is injected into the chamber, causing the tank contents to churn. Bacteria settle and multiply on the sludge particles, digesting a variety of nutrients and oxygen
  A sludge settling chamber where sludge sinks to the bottom of the tank and partially treated water is forced upwards through a mechanism that has another bacteria biomass covering it. This colony of bacteria then consumes most of the oxygen and breaks down any remaining solid particles.
  A purification chamber typically utilizing UV sterilization, chlorination, or ultrafiltration

## Slide 15: Blackwater Systems Aeration-Based Blackwater System

## Slide 16: Blackwater Systems Wetland-Based Blackwater System
Wetland-based blackwater systems depend upon biomimicry and natural processes to filter blackwater. Typically, the system components include;
  An anaerobic settling tank to initially remove large solids from the blackwater
  A biofilter to initially filter the blackwater and reduce odors that may occur in anaerobic conditions
  A series of aerobic tanks containing a variety of algae, organisms, hydroponic plants, plankton, etc. help to process the water, removing fine particles and unwanted bacteria
  A purification chamber typically utilizing UV sterilization, chlorination, or ultrafiltration