## Slide 1: RLL: Relay Ladder Logic
<number>
CONTENTS
1. PLC operation
2. PLC programming
3. Ladder logic
4. Memory and gates
Notes: <number>

## Slide 2: PLC operation
<number>
A PLC has 2 modes of operation
Programming mode: translate engineering language (control logic) to machine language (binary code)
Running (or scanning) mode: Relating the program to inputs and outputs
Notes: <number>

## Slide 3: Programming through standard computer
<number>
Most PLC manufacturers offer software packages that allow a standard computer to be used as a programming terminal
Notes: <number>

## Slide 4: PLC running or scanning mode
<number>
Relating the program to inputs and outputs
The CPU reads the data from the inputs
The program in the CPU uses the inputs to evaluate the control logic. As the program runs, the CPU updates the data
The CPU writes the data to the output
Notes: <number>

## Slide 5: Relating the program to inputs and outputs
<number>
Notes: <number>

## Slide 6: PLC programming
<number>
One of the advantages of PLC is that it can be programmed by non-specialists
Program can be written in the form of a relay ladder diagram represented in terms of contacts and coils.
  Contact: A simple input switch.
  Coil: An output load, e.g., a relay or motor.
current
Switch/contact
coil
Notes: <number>

## Slide 7
Power supply rails drawn as parallel vertical lines on left and right
Connection of rails implies current will flow
An output is “on” when a connection is completed and current flows through the load’s coil
Ladder logic
current
Switch/contact
coil

## Slide 8: Illustration of ladder logic
<number>
Simple control circuit of a bell
Relay Coil
Switch
Associated Relay Ladder
Control circuit
Power circuit

## Slide 9
Simple “always on” load:
        [Always_On = 1] note: sometimes illegal
Load controlled by a single contact:
        [Switch_Con = Switch]
Ladder logic: basic notations

## Slide 10
Boolean logic
  C = A and B also noted C = A.B
C = A or B also noted C = A+B
Ladder logic: AND gate, OR gate

## Slide 11
C = (not A) also noted Ā
A contact with a slash through it is “normally closed.”
This indicates a connection when A is NOT triggered.
So when sensor/input A is activated, there is an open circuit
Ladder logic: NOT gate

## Slide 12
Each rung of the ladder is a statement that is asynchronous when implemented in relay logic, but evaluated sequentially by the PLC.
X = (A+B).(C+D),
Y = Ā.[B+(C.D)]
Ladder logic: basic operations

## Slide 13
<number>
Lamp = SW1 + SW2
Ladder logic: examples

## Slide 14
<number>
<number>
Ladder logic: setting a memory
Switch
“S1” to start
S1
Q1.1
Current flow (Scan 1)
S1
Q1.1
Q1.1
Current flow (Scan 1)
Current flow (Scan 2)
S1
Q1.1
Q1.1
Current flow (Scan 2)
1
2
3
Motor starter
Motor
Input
Output
PLC
Relay Coil “R1”

## Slide 15
<number>
<number>
Setting memory elements
using AND and OR gates
Memory Unit
AND Gate for setting
S1
R1
R1
S3
S2
S1
R1
R1
S3
S2
Memory Unit
OR Gate for setting

## Slide 16
<number>
<number>
Ladder logic: resetting a memory
Motor starter
Motor
Input
Output
PLC
Switches
“S1” to start
“S2” to stop
1
2
3
Relay Coil “R1”
S1
Q1.1
Q1.1
S2
S1
Q1.1
Q1.1
S2
S1
Q1.1
Q1.1
S2

## Slide 17
<number>
<number>
Resetting memory elements
using AND and OR gates
S1
R1
R1
S2
S3
S2 | S3 | S2+S3 | NOT(S2+S3)
0 | 0 | 0 | 1
0 | 1 | 1 | 0
1 | 0 | 1 | 0
1 | 1 | 1 | 0
The only case for current ON is when (S2 is NOT switched ON) AND (S3 is NOT switched ON)

## Slide 18
<number>
<number>
Resetting memory elements
using AND and OR gates
S1
R1
R1
S2
S3
S2 | S3 | S2.S3 | NOT(S2.S3)
0 | 0 | 0 | 1
0 | 1 | 0 | 1
1 | 0 | 0 | 1
1 | 1 | 1 | 0
The only case for current OFF is when (S2 is switched ON) AND (S3 is switched ON)

## Slide 19
<number>
S1
R1
R1
S2
R1
Q1.1
R1
R
G
Ladder logic: adding indicators as outputs

## Slide 20
<number>