## Slide 1: Heat Exchangers

## Slide 2
Heat exchange equipment

## Slide 3: Heating and cooling are common in food operations
Pasteurization
Blanching
Evaporation
Drying
Sterilization
Freezing
Extrusion

## Slide 4
Heat exchangers
Contact type
Steam infusion
Steam injection
Non contact type
Plate
Scraped Surface
Tubular
Shell and Tube

## Slide 5
HE classification: type of medium used
Gas-Gas
Liquid-Gas
Liquid-liquid
HE classification: flow direction
Countercurrent .
Concurrent (parallel).
Countercurrent is more used than concurrent due to its higher efficiency.

## Slide 6
Shell and tube heat exchangers
Examples of heat exchangers

## Slide 7
PLATES Heat Exchangers

## Slide 9
Plate thickness is 0.4 to 0.8 mm
Channel lengths are 2-3 meters
Plates are available in: Stainless Steel, Titanium, Titanium-Palladium, Nickel
PLATES

## Slide 11
Double tube heat exchangers

## Slide 12
One example of this type is the Double pipe heat exchanger.
In this type, the hot and cold fluid streams do not come into direct contact with each other.
They are separated by a tube wall or flat plate.

## Slide 13: Principle of Heat Exchanger
First Law of Thermodynamic: “Energy is conserved.”
0
0
0
0
Control Volume
Qh
Cross Section Area
HOT
COLD
Thermal Boundary Layer

## Slide 14
Q hot
Q cold
Th
Ti,wall
To,wall
Tc
Region I : Hot Liquid-Solid Convection
NEWTON’S LAW OF CCOLING
Region II : Conduction Across Copper Wall
FOURIER’S LAW
Region III: Solid – Cold Liquid Convection
NEWTON’S LAW OF CCOLING
THERMAL
BOUNDARY LAYER
Energy moves from hot fluid to a surface by convection, through the wall by conduction, and then by convection from the surface to the cold fluid.

## Slide 15: Region I : Hot Liquid – Solid Convection
Region II : Conduction Across Copper Wall
Region III : Solid – Cold Liquid Convection
+
U = The Overall Heat Transfer Coefficient [W/m.K]
ro
ri

## Slide 16: Calculating U using Log Mean Temperature
Hot Stream :
Cold Stream:
Log Mean Temperature

## Slide 17
CON CURRENT FLOW
T
1
T
2
T
4
T
5
T
6
T
3
T
7
T
8
T
9
T
10
P
ara
ll
e
l
Fl
ow
Log Mean Temperature evaluation
∆
T
1
∆
T
2
∆ A
A
1
2
Wall

## Slide 18
COUNTER CURRENT FLOW
T
1
T
2
T
4
T
5
T
3
T
7
T
8
T
9
T
10
T
6
Co
un
t
e
r
- C
u
r
re
n
t
F
l
ow
Log Mean Temperature evaluation
T1
A
1
2
T2
T3
T6
T4
T6
T7
T8
T9
T10
Wall

## Slide 19
Heat Exchangers: The Effectiveness – NTU Method

## Slide 20
General Considerations
Computational Features/Limitations of the LMTD
(log mean Temperature difference) Method:
The LMTD method may be applied to design problems for
which the fluid flow rates and inlet temperatures, as well as
a desired outlet temperature, are prescribed.
For a specified H.E. type, the required size (surface area), as well as the other
outlet temperature, are readily determined.
If the LMTD method is used in performing calculations for which
both outlet temperatures must be determined from knowledge of the
inlet temperatures, the solution procedure is iterative.
For both design and performance calculations, the effectiveness-NTU
method (Number of Transfer Units) may be used without iteration.

## Slide 21
Definitions
Heat exchanger effectiveness, 𝓔 ( ratio between actual and max heat transfer) :
New Definitions:
Fluid Heat Capacity Rates
Max possible heat transfer

## Slide 22
Maximum possible heat rate:
Will the fluid characterized by Cmin or Cmax experience the largest possible
temperature change through the HX?
Why is Cmin and not Cmax used in the definition of qmax?
to include maximum feasible heat transfer among the working fluids during calculation

## Slide 23
Heat exchanger effectiveness

## Slide 24
A dimensionless parameter whose magnitude influences H.E. performance:
Number of Transfer Units, NTU:

## Slide 25
Effectiveness – NTU Method
𝓔

## Slide 26
Effectiveness – NTU Method
For Parallel Flow with Cmin = Ch

## Slide 27
Effectiveness – NTU Method
For Parallel Flow with Cmin = Ch

## Slide 28
Effectiveness – NTU Method
For Counterflow with Cr = Cmin/Cmax

## Slide 29
Effectiveness – NTU Method
For Counter-flow with Cr = Cmin/Cmax

## Slide 30
Design Calculations:
For all heat exchangers,
For Cr = 0, (phase change: condensation or evaporation) to all HE types.
Performance Calculations:
Cr

## Slide 34
Effectiveness – NTU Method
Graphical Representations of Equations in Tables 11.3 & 11.4

## Slide 35
Effectiveness – NTU Method

## Slide 36
Effectiveness – NTU Method

## Slide 37
Thermal performance analysis (NTUs) for co- & counter-current exchangers.
Multi-pass exchangers (S&T).
Condensation & boiling.
Radiation.
Heat exchanger selection.

## Slide 38
General Procedure
Must calculate heat duty
Minimise cost subject to constraints
  fluid inlet and outlet temperatures
  allowable pressure drops
  compatibility of materials (corrosion) and fluids (direct/indirect contact)
  maintenance (repairs)
  availability (can we get it easily?)
  sensitivity to other conditions

## Slide 39
General Considerations
Design pressures
Design temperatures
Heat duty / size range
Fluid type / compatibility
Boiling/condensation (“quality”)
Temperature driving forces
Allowable pressure drops
Fouling tendency
Space limitations

## Slide 40
Fundamentals of Heat and Mass Transfer
THEODORE L. BERGMAN, FRANK P. INCROPERA, ADRIENNE S. LAVINE, DAVID P. DEWITT
http://books.google.com.sa/books?hl=ar&lr=&id=vvyIoXEywMoC&oi=fnd&pg=PR21&dq=table+11.3+heat+exchanger+effectiveness+relations&ots=8HqjQScVI8&sig=eA2YjAcHwA8A1ls-CFT6RNEU8hY&safe=on&redir_esc=y#v=onepage&q=table%2011.3%20heat%20exchanger%20effectiveness%20relations&f=false